## Arhitectural solutions
No. | Type of equipment requested by BoQ and its data | Bidder’s response
|  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03226 Capital repair and modernization of the “Emil Nicula” Theoretical Lyceum from Mereni village, Anenii Noi district (First phase)
1 | Suspended ceilings made of prefabricated panels including grid system with physical and visual characteristics type Rockfon Artic E24/ or equvalent with partially visible structure and dimensions 600 x 600 x 15mm, class 1/C/0N according to EN 13964
2 | Plastic floors mounted on the existing substrate, cleaned, including PVC sills, in rooms with areas greater than 16 sqm, with PVC carpet glued with pre-bonded / Omogenius PVC carpet, thickness = 2-2,3 mm; change:PVC profile, PVC sill in PVC PVC connection profile R=30 mm - 0,6 m/m2. Color according to the design.
3 | Epoxy flooring system with a total thickness of 2.0 mm, with anti-slip effect, applied on an existing substrate. The flooring shall be of self-leveling or multilayer epoxy type, applied on a properly prepared concrete substrate.The flooring shall have a total thickness of 2.0 mm (±10%), with anti-slip classification in the range of R10–R12. Mechanical properties shall include compressive strength of at least 70–90 MPa, flexural strength of at least 30 MPa, and adhesion to the substrate of at least 1.5–2.0 MPa (with failure in concrete). The system shall be impermeable to liquids, with negligible water absorption, and resistant to water, cleaning agents, oils, fuels, diluted acids and alkalis, as well as de-icing salts. The flooring shall maintain performance within a service temperature range of approximately -10°C to +60°C. The material shall comply with fire reaction class Bfl-s1 according to EN 13501-1 and meet low VOC emission requirements suitable for indoor environments.
4 | Interior partitions made of aluminum profiles with mat sandwich filling composed of PU boards and 1 mm sheet metal on both sides. The windows will be made of 4+4 mm transparent triplex glass. Doors will be equipped with stainless steel door handle set, Hafele Startec model LTD 2170 (or smilar); C-3 7500x2150(h)
5 | WC cubicles, H = 2.0 m, made of aluminum profiles with 12 mm HPL infill (color according to design solutions) and stainless steel support elements, for buildings up to 35 m in height, including fixed panels and door leaves.
6 | Interior wooden doors in a can, with 2 mm metal frame, color RAL 7014 and 44 mm plywood laminated wood plywood canvas, color RAL 1014 with mat varnish. With 1 mm stainless steel protection plate at the bottom and 4+4 mm transparent triplex glass 4+4 mm and stainless steel door handle set, Hafele Startec model LTD 2170 (or smilar); UI-1 1150x2020(h)

## Elevator
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03226 Capital repair and modernization of the “Emil Nicula” Theoretical Lyceum from Mereni village, Anenii Noi district. First phase.
1 | Elevator NIKAN 5000 MRL
| Model | AEP -634, Q=630kg, V= 1m/s (Machine Room-Less) or equivalent
| Type | Electric traction elevator
| Rated load | 630 kg
| Passenger capacity | 2 persons
| Number of stops | 3
| Rated speed | 1.0 m/s
| Drive system | Gearless traction machine
| Machine room | Without (MRL configuration)
| Control system | Microprocessor-based collective control
| Power supply | 380–400V, 3-phase, 50 Hz
| Door type | Automatic sliding doors (center opening)
| Door opening width | Minim 900 mm (standard for 600 kg) with access for persons with disabilities
| Cabin internal dimensions | Minim 1100 × 1400 mm (W × D)
| Shaft dimensions (min.) | Approx. 1600 × 1600 mm (acording drawings)
| Pit depth | Approx. 1200 mm (typical)
| Overhead height | Approx. 3600 mm (typical)
| Safety system | Overspeed governor, safety gear, door interlocks
| Drive control | VVVF (Variable Voltage Variable Frequency)
| Noise level | Low-noise operation
| Compliance | EN 81-20 / EN 81-50 (or local equivalent)
| Interior finish | Stainless steel (as per design)
| Lighting | LED ceiling lighting
| Emergency system | Emergency lighting & alarm
| Optional features | ARD (Automatic Rescue Device), GSM module, access control

## Water
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03226 Capital repair and modernization of the “Emil Nicula” Theoretical Lyceum from Mereni village, Anenii Noi district. First phase.
1 | Public WC Pan (Side Outlet, Floor-Mounted)
| Product type | Floor-mounted WC pan for public/sanitary facilities
| Outlet type | Horizontal (side/back outlet)
| Installation type | Floor-standing
| Material | Sanitary porcelain / semi-porcelain, glazed finish
| Surface treatment | Smooth, antibacterial glaze, easy to clean
| Flushing system | Washdown or rimless flushing system
| Flush volume | 6/3 L dual flush (or 6 L single flush)
| Cistern type | Close-coupled cistern mounted directly on the bowl
| Cistern material | Ceramic (matching bowl)
| Water inlet | Bottom or side inlet (½")
| Flush mechanism | Mechanical push-button (dual flush recommended)
| Seat and cover | Heavy-duty thermoplastic or duroplast, slow-close (optional)
| Fixing system | Floor fixing bolts with protective caps
| Trap type | P-trap (horizontal outlet)
| Outlet diameter | Ø100 mm
| Dimensions (approx.) | 650–700 mm (L) × 350–380 mm (W) × 750–800 mm (H)
| Water pressure range | 0.5 – 10 bar
| Color | White (standard)
| Compliance | EN 997 / EN 33 (European standards)
| Application | Public buildings, schools, offices, commercial spaces
2 | Public washbasin (lavatory) made of semi-porcelain / sanitary porcelain, mounted on pedestal, with PP siphon
| Product type | Washbasin for public sanitary facilities
| Installation type | Wall-mounted basin with full pedestal
| Material | Sanitary porcelain / semi-porcelain, glazed finish
| Surface treatment | Smooth, hygienic, stain-resistant glaze
| Mounting method | Wall-fixed with anchor bolts; pedestal for aesthetic and pipe concealment
| Pedestal type | Full pedestal (ceramic), matching basin
| Basin dimensions (approx.) | 550–600 mm (W) × 450–500 mm (D)
| Height (installed) | Approx. 800–850 mm from finished floor level
| Tap hole | Single hole Ø35 mm (standard)
| Overflow | Integrated overflow system
| Waste outlet diameter | Ø45 mm
| Siphon | Bottle trap, polypropylene (PP), Ø32 mm
| Water supply connection | ½" flexible connectors
| Fixing kit | Included (bolts, plugs, caps)
| Color | White (standard)
| Water pressure range | 0.5 – 10 bar
| Compliance | EN 14688 (washbasins)
| Application | Public buildings, offices, schools, commercial premises
3 | Wall-Mounted Urinal (Sanitary Porcelain)
| Product type | Urinal for public sanitary facilities
| Installation type | Wall-mounted
| Mounting surface | Reinforced concrete wall
| Material | Sanitary porcelain, fully glazed
| Surface treatment | Smooth, hygienic, stain- and chemical-resistant glaze
| Flushing system | Top or rear inlet (exposed or concealed flush valve)
| Flush control | Manual push valve or automatic sensor (optional)
| Water consumption | 0.5 – 3.0 L per flush (depending on flush valve)
| Water inlet connection | ½"
| Outlet type | Horizontal or vertical outlet
| Waste outlet diameter | Ø50 mm
| Trap type | Integrated trap or external siphon
| Fixing system | Wall anchor bolts with concealed fixings
| Installation height | Rim approx. 600–650 mm above finished floor level
| Dimensions (approx.) | 300–360 mm (W) × 300–350 mm (D) × 500–600 mm (H)
| Color | White (standard)
| Water pressure range | 0.5 – 10 bar
| Compliance | EN 13407 (urinals)
| Application | Public buildings, schools, offices, commercial facilities
4 | Chrome-Plated Mixer Tap with Swivel Spout (Public Toilets)
| Product type | Basin mixer tap for public sanitary facilities
| Installation type | Deck-mounted (single-hole installation)
| Body material | Brass (CuZn), chrome-plated finish
| Surface finish | Polished chrome, corrosion-resistant
| Spout type | Swivel (pivoting) spout
| Spout reach | Approx. 150–200 mm
| Cartridge type | Ceramic cartridge, 35–40 mm
| Control type | Single-lever mixer
| Water supply connection | Flexible hoses ½"
| Aerator | Anti-limescale aerator, M24/M22
| Flow rate | 5–9 L/min (depending on pressure)
| Operating pressure | 1 – 10 bar
| Recommended pressure | 3 bar
| Water temperature range | 5°C – 90°C
| Fixing system | Mounting kit included (gasket, fixing nut, bolts)
| Application | Public toilets, schools, offices, commercial buildings
| Compliance | EN 817 (mechanical mixer taps)
5 | Accessible Wall-Mounted Bath Mixer with Hand Shower
| Product type | Bath mixer tap with hand shower for accessible sanitary rooms
| Installation type | Wall-mounted
| Mounting surface | Brick masonry wall (with concealed pipe connections)
| Body material | Brass (CuZn), chrome-plated
| Surface finish | Polished chrome, corrosion-resistant
| Control type | Single-lever mixer with extended ergonomic handle (accessible use)
| Cartridge type | Ceramic cartridge, 35–40 mm
| Temperature limiter | Adjustable safety stop (anti-scald protection)
| Diverter | Integrated automatic diverter (bath/shower)
| Shower hose | Flexible stainless steel or reinforced PVC, length 1500–2000 mm
| Hand shower | Ergonomic hand shower, anti-limescale nozzles
| Water inlet connection | ½" standard eccentric connections
| Flow rate | 8–12 L/min
| Operating pressure | 1 – 10 bar
| Recommended pressure | 3 bar
| Temperature range | 5°C – 90°C
| Installation height | According to accessibility standards (approx. 900–1100 mm from finished floor)
| Accessibility compliance | EN 12182 / EN 1111 (if thermostatic version)
| Safety features | Anti-scald device, smooth edges, easy-grip lever
| Application | Public buildings, accessible sanitary units, healthcare facilities
| Color | Chrome (standard)

## HAVC
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03226 Capital repair and modernization of the “Emil Nicula” Theoretical Lyceum from Mereni village, Anenii Noi district. First phase.
1 | Steel Panel Radiator Type “Therm-x2 Profil K 22", 500×1000 or equivalent
| Product type | Steel panel radiator
| Model | Type 22K (two panels + two convectors)
| Dimensions (H × L) | 500 × 1000 mm
| Depth | Approx. 100 mm
| Material | Cold-rolled steel panels
| Surface finish | Powder-coated, white (RAL 9016 standard)
| Heat output (90/70/20°C) | Approx. 1850 W
| Heat output (75/65/20°C) | Approx. 1450 W
| Maximum operating temperature | 110°C
| Maximum working pressure | 10 bar
| Test pressure | 13 bar
| Water content | Approx. 5–6 liters
| Weight | Approx. 25–26 kg
| Connections | 4 × G 1/2" female threaded (side connections)
| Installation type | Wall-mounted (brackets included)
| Air vent & plug | Included
| Standard compliance | EN 442
2 | Steel panel radiator “Therm-x2 Profil K 22" 500×500 or equivalent
| Product type | Steel panel radiator
| Model | Type 33K (three panels + three convectors)
| Dimensions (H × L × D) | 500 × 1100 × ~155 mm
| Material | Cold-rolled steel panel construction
| Surface finish | Powder-coated white (standard RAL, corrosion-protected)
| Heat output (90/70/20 °C) | ~2914 W
| Heat output (75/65/20 °C) | ~2287 W
| Water content | ~8.36 L
| Weight | ~50.5 kg
| Maximum operating temperature | 110 °C
| Maximum working pressure | 10 bar
| Test pressure | 13 bar
| Connections | 4 × G 1/2″ internal threads
| Connecting pitch | H – 54 mm
| Installation type | Wall-mounted radiator
| Compliance | EN 442 (European radiator standard)
3 | Caleffi 401 thermostatic angle valve for radiators F 1/2 401402 or equivalent
| Product type | Thermostatic radiator valve with pre-setting
| Model | RTR-N
| Nominal diameter | DN 15 (≈ 1/2″)
| Connection type | Rp 1/2″ internal thread
| Valve configuration | Normal flow type (presetting on the radiator inlet)
| Body material | Brass with corrosion-resistant surface finish
| Presetting | Integrated presetting ring with adjustable Kv steps
| Kv range | Approx. 0.04 – 0.7 m³/h (depending on presetting position)
| Kv at presetting “N” | Approx. 0.73 m³/h
| Max. operating temperature | Up to 120 °C
| Max. working pressure | 10 bar
| Test pressure | 16 bar
| Seal material | EPDM or equivalent elastomer
| Differential pressure tolerance | Up to ~0.6 bar for stable control
| Surface finish | Nickel-plated or chrome plated (depending on manufacturer)
| Standards compliance | EN 215 (Thermostatic radiator valves)
| Accessories | Compatible with thermostatic heads (RA, RAS series or equivalent)
4 | Caleffi Radiator Valve Lockshield Straight 1/2" or equivalent
| Product type | Radiator shut-off / lockshield valve
| Connection size | R 1/2″ (internal thread) – radiator and system connections
| Design | Straight lockshield valve
| Body material | Brass with nickel-plated finish (corrosion-resistant)
| Maximum operating temperature | 120 °C
| Maximum working pressure | 10 bar
| Test pressure | 16 bar
| Kv (flow coefficient) | Approx. 2.20–2.50 m³/h
| Seal material | EPDM or equivalent
| Surface finish | Nickel plated
| Thread standard | ISO 7/1 (R 1/2″)
| Type variants | Straight or angled, standard or self-sealing tailpiece
5 | Thermostatic control head calefii or equivalent
| Type | Thermostatic radiator thermostat element
| Application | For automatic temperature control of radiator valves
| Compatibility | Designed for RTR series radiator valves (e.g., RTR-N, RTR-G), can be combined with appropriate radiator valve bodies
| Sensing element | Gas-filled bulb sensor
| Mounting / Connection | Clip-on type (quick clip fitting to valve)
| Adjustment range (room air temperature) | 5 °C to 26 °C
| Temperature range, operational | Min. 5 °C – Max. 26 °C setpoint range
| Colour | White
| Max. permitted system temperature | Approx. 120 °C (typical TRV rating for paired valves)
| Max. working pressure | Approx. 10 bar (based on typical radiator thermostatic valve ratings)
| Ratio / Sensitivity | Proportional direct-acting thermostat with small proportional band
| Housing material | Plastic body with internal sensing element
| Warranty | Approx. 1 year
| Country of manufacture | Denmark (Danfoss)
| Standards compliance | EN 215 (when combined with compliant radiator valve)
6 | M66457.6 - Meiflow L MF 2300 Brass Distribution (DN 200x3) or equivalent
| Product type | Distribution manifold / collector
| Model | R551 – Brass distribution manifold or equivalent
| Nominal size | DN 200 (4 ″) main inlet/outlet connections
| Number of outlets | 6 circuits (6 derivations)
| Outlet connection size | Typically 1 ″ female threaded outlets (applicable to DN 50 variant)
| Material | Brass (CW605N)
| Outlet spacing | 100 mm center-to-center between outlets
| Temperature range | 5 °C – 110 °C
| Maximum working pressure | 16 bar
| Test pressure | Typically above working pressure (manufacturer standard)
| Connection thread type | Female threaded (G)
| Material grade | CW605N brass (corrosion-resistant)
| Mounting | Wall mounting with appropriate brackets ( R588P)
| Suitable fluid | Hot and chilled water (heating/cooling systems)
7 | Caleffi Ball Valve, PN 16, DN 25 or equivalent
| Product type | Ball shut-off valve (stop valve)
| Model / Series | Caleffi ball valve, PN 16, DN 25 or equivalent
| Nominal size | DN 25 (1″)
| Pressure rating | PN 16 (maximum working pressure 16 bar)
| Connection type | Threaded / flanged (depending on version)
| Body material | Brass (corrosion-resistant)
| Ball material | Brass, chrome-plated
| Seat / seals | PTFE (Teflon) seats
| Stem material | Stainless steel or brass
| Handle | Lever handle for manual operation
| Bore type | Full bore (unrestricted flow)
| Medium temperature range | Approx. –10 °C to +100 °C (typical for PN 16 valves)
| Suitable medium | Hot and cold water, glycol solutions, non-aggressive fluids
| Standards / Compliance | EN 12266 (valve testing), DIN/ISO standards for threaded/flanged connections
| Installation | Inline with pipework, vertical or horizontal
| Application | Heating systems, plumbing, hydronic circuits
8 | Inline centrifugal duct fan with EC motor - Blauberg Centro 250EC or equivalent
| Type | Inline centrifugal duct fan
| Motor type | EC (electronically commutated)
| Duct connection diameter | 250 mm
| Power supply | 220–250 V, 1~ phase
| Frequency | 50 / 60 Hz
| Power consumption | 160–165 W
| Current | 1.1–1.15 A
| Maximum airflow | 1200–1250 m³/h
| Maximum airflow | 340–347 l/s
| Maximum static pressure | up to 600 Pa
| Fan speed | ~2600–2900 rpm
| Sound pressure level (at 3 m) | 46–48 dB(A)
| Protection class | IPX4
| Max transported air temperature | -25 … +60 °C
| Speed control | 0–10 V (BMS compatible)
| Motor protection | Overheating protection with auto restart
| Casing material | Polymer-coated steel / ABS
| Impeller type | Centrifugal, backward-curved blades
| Installation type | Inline (horizontal/vertical)
| Weight | approx. 4.3–5.8 kg
| Compliance | ErP 2018 compliant
9 | Mitsubishi Heavy FDT50VH cassette indoor unit or equivalent
| Type | 4-way cassette indoor unit (VRF / multi-split)
| Cooling capacity (nominal) | 5.0 kW (1.1–5.6 kW)
| Heating capacity (nominal) | 5.4 kW (0.6–6.3 kW)
| Power supply | 1~ / 220–240 V / 50–60 Hz
| Power consumption (cooling/heating) | 1.29 / 1.31 kW
| EER / COP | 3.88 / 4.12
| Max current | 15 A
| Starting current | 5A
| Airflow (high–low) | 19–10 m³/min
| Sound pressure level (indoor) | 26–36 dB(A)
| Sound power level (indoor) | 55–56 dB(A)
| Sound pressure level (outdoor) | 49–50 dB(A)
| Sound power level (outdoor) | 63 dB(A)
| Dimensions indoor unit (HxWxD) | 236 × 840 × 840 mm
| Panel dimensions | 35 × 950 × 950 mm
| Outdoor unit dimensions | 640 × 800 × 290 mm
| Weight indoor | 24 kg (unit 19 kg + panel 5 kg)
| Weight outdoor | 45 kg
| Refrigerant type | R410A
| Refrigerant piping (liquid/gas) | 6.35 mm (1/4") / 12.7 mm (1/2")
| Max piping length | 30 m
| Max height difference | 20 m
| Operating temperature (cooling) | -15 … +46 °C
| Operating temperature (heating) | -20 … +24 °C
10 | Mitsubishi Heavy SCM100ZM-S or equivalent
| Type | Multi-split outdoor unit (inverter)
| Application | Residential / commercial multi-room systems
| Power supply | 1~ / 220–240 V / 50 Hz
| Cooling capacity (nominal) | 10.0 kW (1.8–12.0 kW)
| Heating capacity (nominal) | 12.0 kW (1.5–13.5 kW)
| Power consumption (cooling/heating) | 2.86 / 2.93 kW
| EER (cooling) | 3.5–4.1
| COP (heating) | up to 4.1
| Maximum current | up to 29 A
| Recommended circuit breaker | 32 A
| Number of connectable indoor units | 2 – 5 units
| Total indoor unit capacity | up to 16.0 kW
| Airflow | approx. 75 m³/min
| Sound pressure level | 56–59 dB(A)
| Sound power level | 68–71 dB(A)
| Dimensions (H×W×D) | 945 × 970 × 370 mm
| Weight | 92 kg
| Refrigerant type | R410A
| Refrigerant charge | 6.0 kg
| Refrigerant piping (liquid) | 6.35 mm (1/4") × up to 5
| Refrigerant piping (gas) | 9.52 mm (3/8") × up to 5
| Max piping length (total) | up to 90 m
| Max piping length (single unit) | 25 m
| Max height difference | 20 m
| Operating temp. (cooling) | -15 … +43 °C
| Operating temp. (heating) | -15 … +24 °C
11 | Ceiling swirl diffuser (anemostat) with plenum box MANDIK VAPM 315K/D/T/P/R (180) or equivalent
| Type | Ceiling swirl diffuser (anemostat) with plenum box
| Application | Air supply / exhaust in ventilation and air-conditioning systems
| Nominal size | Ø315 mm
| Front panel type | Circular (K)
| Front plate execution | With diffuser (D)
| Airflow direction | Supply air (P) / exhaust possible
| Connection type | Horizontal connection (T)
| Regulation | With regulating damper (R)
| Neck diameter | 315 mm
| Airflow range | approx. 300 – 900 m³/h (depending on pressure)
| Recommended air velocity | up to 4–6 m/s
| Pressure loss | approx. 20 – 80 Pa
| Throw pattern | Swirl air distribution (360°)
| Installation | Ceiling-mounted (false ceiling)
| Material (diffuser) | Powder-coated steel
| Material (plenum box) | Galvanized steel
| Finish | White RAL 9010 (standard)
| Temperature range | up to +60 °C
| Noise level | Low, depending on airflow and pressure
| Accessories | Plenum box, damper, insulation, flexible connection
| Fire resistance option | (180) – compatible with EI180 fire-rated systems (depending on configuration)
12 | Air Handling Unit with Heat Recovery (MANDIK) L=14,000/13,000 m³/h, P=500/500 Pa, Rotor=75.9%, or equivalent
| Equipment type | Air Handling Unit (AHU) with rotary heat recovery
| Installation | Outdoor (weatherproof execution)
| Airflow – supply air (L) | 14,000 m³/h
| Airflow – extract air (L) | 13,000 m³/h
| External static pressure (supply/extract) | 500 / 500 Pa
| Heat recovery type | Rotary heat exchanger (rotor)
| Heat recovery efficiency | Minim 0.759
| Heating coil type | Water heating coil
| Heating medium | Hot water 60 / 40 °C
| Heating capacity (Qt) | 80.8 kW
| Cooling coil type | Direct expansion (DX) / refrigerant coil
| Cooling capacity (Qx) | 155.4 kW
| Refrigerant type | Freon (depending on system design)
| Filters (supply/extract) | G4 / G4 bag-type filters
| Fan type | EC plug fans (high efficiency)
| Motor type | Electronically commutated (EC)
| Casing construction | Double-skin panels, thermal & acoustic insulation
| Casing thickness | 40–60 mm (typical)
| Panel insulation | Mineral wool or PU foam
| Casing airtightness | Class L2 or better
| Thermal bridging | Class TB2 or better
| Control system | Integrated автомatics / BMS compatible
| Frost protection | Included (rotor + coil protection)
| Drain system | Condensate tray with drainage
| Noise level | Low-noise execution (per project requirements)
| Power supply | 380–400 V / 3~ / 50 Hz
| Protection class | IP54 (outdoor execution)
| Operating temperature | Suitable for outdoor climatic conditions
| Accessories | Mixing section, dampers, silencers, sensors
13 | Galvanized steel pipe DN80 (Ø ~88.9 mm) Viega Megapress system or equivalent
| Type | Press fitting system for steel pipes
| Applicable pipe | Galvanized steel pipe (zinc-coated)
| Nominal diameter | DN80 (≈ 3")
| Outside diameter | ~88.9 mm
| Pipe standard | EN 10255 / EN 10216 / EN 10217
| Pipe wall thickness | Schedule 10 – 40 (typical)
| Connection method | Cold press connection (no welding/threading)
| Fitting material | Non-alloy steel 1.0308
| Coating | Zinc-nickel corrosion protection
| Sealing element | EPDM (standard) / FKM (high temp / oil)
| Mechanical locking | Stainless steel cutting ring
| Nominal pressure | PN16
| Max operating temperature | up to 105 °C (EPDM)
| Application | Heating, cooling, compressed air, industrial systems
| Compatibility | Black, galvanized, painted, coated steel pipes
| Installation tools | Viega Pressgun + press rings
| Installation method | Cold pressing (no flame)
| Leak detection | SC-Contour (unpressed leakage indication)
| Fire safety | No hot works required
| Standards | DIN EN 12828, VDI 2035
14 | Flamco Special distributor 2.3000 DN200–DN100 or equivalent
| Product type | Hydraulic distributor / manifold (low-loss header / collector)
| Model | Special distributor 2.3000
| Configuration | DN200 main header with DN100 branch connection
| Nominal diameter (primary) | DN200
| Nominal diameter (secondary) | DN100
| Outside diameter (primary) | 219.1 mm
| Outside diameter (secondary) | 114.3 mm
| Number of circuits | 1 circuit (modular expandable)
| Hydraulic capacity | up to approx. 2,300 kW
| Flow rate (typical) | up to ~55 m³/h
| Design velocity | ~1.3 m/s (reference condition)
| Maximum operating pressure | PN10 (10 bar)
| Maximum temperature | up to 110 °C
| Material | Carbon steel (painted / coated)
| Construction | Two-chamber design (hydraulic separation of supply/return)
| Surface treatment | Painted / coated steel
| Insulation | Factory insulated
| Connections | Groove / clamp (Big-Fix / Victaulic type)
| Installation | Floor-mounted (with adjustable supports)
| Orientation | Horizontal
| Length | approx. 735 mm
| Height | approx. 1080 mm
| Depth | approx. 390 mm
| Included accessories | End caps, clamps, insulation, mounting supports
| Application | Heating and cooling water systems
| Medium | Water / glycol mixtures
15 | Hydraulic distributor Flamco Meiflow LMF 2300 or equivalent
| Type | Hydraulic distributor / manifold (low-loss header system)
| Series | Meiflow L-Line (large systems)
| Application | Heating / cooling water distribution
| Thermal capacity | up to 2300 kW
| Nominal diameter (primary) | DN200
| Branch connections | DN80 / DN100 (depending on version)
| Number of heating circuits | 1–2 circuits (modular expandable)
| Design | Thermally separated chambers
| Max operating pressure | PN10
| Max operating temperature | up to 110 °C
| Medium | Water / water-glycol mixtures
| Material | Steel (painted / coated)
| Surface protection | Anti-corrosion coating
| Insulation | Factory insulated
| Connections | Clamp / groove type (BigFixLock / Victaulic)
| Installation type | Floor-mounted (monoblock)
| Width | approx. 735 mm
| Height | approx. 1080 mm
| Depth | approx. 390 mm
| Mounting | With support legs and fixing elements
| Accessories included | End caps, clamps, insulation, mounting kit
| Compatibility | Meiflow pump groups (DN40–DN100)
| System integration | Modular system (expandable with additional circuits)
16 | Belimo R3050S4 + NR24ASR 3 way valve or equivalent
| Type | 3-way control ball valve with modulating actuator
| Application | Heating / cooling water systems
| Nominal diameter | DN50
| Connection type | Internal thread Rp 2"
| Valve type | 3-way changeover / mixing valve
| Nominal pressure | PN25
| Kvs value | 25–49 m³/h (depending on version)
| Medium | Water / water-glycol (max. 50%)
| Fluid temperature | -10 … +120 °C
| Close-off pressure | up to 1400 kPa
| Recommended Δp | ≤200 kPa (low-noise operation)
| Leakage rate | Class A (tight shut-off) / Class I
| Flow characteristic | Equal percentage / linear
| Actuator model | NR24ASR
| Actuator torque | 20 Nm
| Control signal | 2–10 V modulating
| Supply voltage | AC/DC 24 V
| Running time | ~90 s (90° rotation)
| Power consumption | ~2.5 W (operation)
| Protection class | IP54
| Auxiliary switch | Integrated (depending on version)
| Mounting | Direct mounting on valve
| Control type | Modulating (BMS compatible)
| Safety function | Optional fail-safe (depending on variant)
17 | Gasketed plate heat exchanger (GPHE) Alfa Laval AQ4L-FG (16 bar) - or equivalent
| Product type | Gasketed plate heat exchanger (GPHE)
| Model | AQ4L-FG
| Series | AlfaQ (AHRI certified)
| Application | Heating and cooling (HVAC, district systems)
| Design pressure | 16 bar (FG frame, PED)
| Max design temperature | up to 180 °C
| Carrying bar length | 1200 mm
| Frame type | FG (standard industrial frame)
| Plate type | AQ4L
| Heat transfer principle | Counter-current flow, plate heat exchange
| Flow capacity | up to ~50 kg/s (≈180 m³/h)
| Connections | Flanged DN50–DN100 (EN 1092-1 PN16 typical)
| Plate material | Stainless steel (AISI 316 / 304 typical)
| Gasket material | EPDM / NBR (depending on medium)
| Mounting | Floor-mounted frame construction
| Maintenance | Openable frame for cleaning and plate replacement
| Pressure vessel standard | PED
| Certification | AHRI certified performance
| Configuration | Adjustable (number of plates can be modified)
18 | 2-way shut-off valve (butterfly / wafer type) Belimo A6100H - or equivalent
| Type | 2-way shut-off valve (butterfly / wafer type)
| Application | Heating and cooling systems (on/off control)
| Nominal diameter | DN100
| Connection type | Wafer type (for flanged installation)
| Nominal pressure | PN6 / PN10 / PN16
| Kvs value | up to 580 m³/h
| Medium | Water / water-glycol mixtures
| Fluid temperature | -20 … +120 °C (max. 130 °C short-term)
| Valve body material | Cast iron (GGG40)
| Disc material | Stainless steel (SS304)
| Seal material | EPDM
| Leakage rate | Tight shut-off (ISO class)
| Operation | On/Off (with actuator)
| Manual override | Yes (lever included)
| Installation | Between flanges (wafer mounting)
| Mounting position | Horizontal / vertical (actuator on top)
| Control compatibility | Actuators (rotary type)
| Application scope | Chillers, boilers, AHU coils, distribution systems
19 | Circular fire damper (smoke/fire protection) MANDIK FDMS S225-40 - or equivalent
| Type | Circular fire damper (smoke/fire protection)
| Application | HVAC ducts – fire compartment separation
| Nominal diameter | Ø225 mm
| Installation | In duct (wall / ceiling penetration)
| Fire resistance class | up to EI 90 S
| Standard compliance | EN 15650
| Fire test standard | EN 1366-2
| Classification | EN 13501-3+A1
| Max air velocity | up to 12 m/s
| Max pressure difference | up to 2500 Pa
| Operating temperature (ambient) | -30 … +50 °C
| Leakage class (casing) | Class C
| Internal leakage | Class 2 (EN 1751)
| Control type | With actuator (.40 version – motorized)
| Actuator supply | 24 V or 230 V (depending on configuration)
| Safety mechanism | Thermal fuse ( 95°C)
| Operation | Normally open – closes on fire / power loss
| Position feedback | Open/Closed signal switches
| Material | Galvanized steel casing
| Corrosion resistance | According to EN 15650
| Maintenance | Accessible inspection / reset
| Certification | CE marked
20 | Rectangular tight regulation damper MANDIK RKTM 1000×1000.45 - or equivalent
| Type | Rectangular tight regulation damper
| Application | Airflow control and shut-off in rectangular ducts
| Duct size | 1000 × 1000 mm
| Construction | Multi-blade opposed blade damper
| Control type | Electric actuator (2-position)
| Version code | .45 – actuator 230 V, without position feedback
| Airflow function | Regulation + tight shut-off
| Max air velocity | up to 12 m/s
| Max pressure difference | 1200 – 1500 Pa
| Leakage class (casing) | Class C (EN 1751)
| Internal leakage | Class 2
| Operating temperature | -20 … +80 °C
| Material | Galvanized steel
| Blade sealing | Silicone sealing (tight execution)
| Blade width | approx. 100 mm
| Shaft material | Steel / plastic bearings
| Installation | In rectangular duct (any position)
| Connection | Flanged connection to duct
| Actuator supply | 230 V AC
| Control mode | On/Off (open/close)
| Optional versions | Manual / modulating / fail-safe variants available

## Electrical
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03226 Capital repair and modernization of the “Emil Nicula” Theoretical Lyceum from Mereni village, Anenii Noi district. First phase.
1 | Recessed LED Panel, 600×600 mm, 35 W, 4000 K
| Product type | Recessed LED ceiling luminaire (LED panel)
| Model / Format | 600 × 600 mm (suitable for 600×600 mm ceiling grid)
| Rated power | 35 W
| Light source | Integrated LED modules
| Color temperature | 4000 K (neutral white)
| Rated luminous flux | ≈ 3000–3500 lm (typical from a 35 W panel)
| Efficacy | ≈ 85–100 lm/W (dependent on manufacturer)
| CRI (Color Rendering Index) | ≥ 80 (≥ Ra80)
| Beam angle | ≈ 120° (wide uniform distribution)
| Driver type | External / integrated LED driver (electronic)
| Input voltage | 220–240 V AC, 50/60 Hz
| Power factor | ≥ 0.90
| Dimmable | Optional (DALI / 1–10 V / phase-cut, manufacturer dependent)
| Housing material | Aluminium frame + steel back housing
| Diffuser / Optics | Opal / microprismatic diffuser for uniform glare-free light
| Mounting type | Recessed into suspended ceiling grid (T-bar)
| Protection class | IP20 (indoor use)
| IK rating | IK04–IK05 (impact resistance)
| Operating temperature | 0 °C to +40 °C
| Lifetime | ≥ 50,000 h (L80 B10)
| Certifications | CE
| Finish / Color | White frame (powder coated)
2 | Linear LED Light, 1200 mm, 45 W, 4000 K
| Product type | Linear LED luminaire
| Length | 1200 mm
| Rated power | 45 W
| Light source | Integrated LED
| Color temperature | 4000 K (neutral white)
| Luminous flux | ≈ 3900–4500 lm (typical from a 45 W LED)
| Efficacy | ≈ 85–100 lm/W (dependent on model)
| Color rendering (CRI) | ≥ 80 (≥ Ra80)
| Beam angle | 120° (wide light distribution)
| Driver type | Built-in / external electronic LED driver
| Input voltage | 220–240 V AC, 50/60 Hz
| Power factor | ≥ 0.90
| Dimmable | Optional (DALI / 1–10 V / phase-cut – model dependent)
| Housing material | Aluminium body with steel end caps
| Diffuser | Opal or prismatic polycarbonate for uniform light
| Protection class | IP20 (indoor use)
| IK rating | IK04–IK05 (impact resistant)
| Operating ambient temp | 0 °C to +40 °C
| Lifetime | ≥ 50,000 h (L80)
| Finish / Color | White (standard)
| Certifications | CE, RoHS, EMC
| Application | Offices, corridors, retail, education, industrial interiors
3 | Illuminated Direction Indicator with Battery
| Product type | Illuminated directional indicator / emergency exit arrow sign
| Rated LED power | 3 W
| Light source | High-efficiency LEDs
| Illumination color | Green (standard for emergency direction signs)
| Symbol / Arrow type | Directional arrow or pictogram (configurable: left / right / up / down)
| Supply voltage | 220–240 V AC, 50 Hz (primary mains)
| Backup power | Rechargeable battery (internal)
| Battery type | Sealed lead-acid (SLA) or NiMH (model dependent)
| Battery autonomy | ≥ 3 hours (in emergency mode)
| Charge time | ≤ 24 hours to full charge
| LED lifetime | ≥ 50,000 h
| Viewing distance | ≥ 20–25 m (depending on size and installation)
| Ingress protection | IP20 (indoor), optional higher rating on request
| Mounting | Wall or ceiling (surface mounted)
| Housing material | ABS / polycarbonate flame-retardant enclosure
| Operating temperature | 0 °C to +40 °C (typical)
| Emergency testing | Built-in test button (optional)
| Standards / Compliance | Compliant with EN 50172 / EN 1838 (emergency lighting)
| Indicators | Charge / test LED indicators
| Finish / Color | White housing (standard)
4 | Distribution Board, 36 Modules (Flush-Mounted)
| Product type | Electrical distribution board (consumer unit)
| Model / Type | Flush-mounted distribution board, 36 modules (ЩРв-36 or equivalent)
| Installation type | Recessed / flush-mounted (in-wall installation)
| Number of modules | 36 DIN modules (3 rows × 12 modules typical)
| Rated voltage | 230/400 V AC, 50 Hz
| Rated current | Up to 63–100 A (depending on manufacturer)
| Protection class | IP30–IP40 (indoor use)
| Impact resistance | IK07 (typical)
| Material | Metal enclosure with powder coating or high-quality ABS (model dependent)
| Door type | Solid or transparent hinged door
| Mounting rail | Standard 35 mm DIN rail
| Neutral busbar (N) | Included
| Protective earth busbar (PE) | Included
| Terminal type | Screw terminals
| Cable entry | Top and bottom knockouts
| Operating temperature | –5 °C to +40 °C
| Color | White (RAL 9016 typical)
| Standards / Compliance | IEC 61439-1 / IEC 61439-3, CE
5 | Residual Current Circuit Breaker with Overcurrent Protection (RCBO), 2P, C16A, 10 mA, 6 kA
| Product type | RCBO (Residual Current Circuit Breaker with Overcurrent protection)
| Number of poles | 2P (Phase + Neutral)
| Rated current (In) | 16 A
| Tripping characteristic | Type C (magnetic curve C)
| Rated residual current (IΔn) | 10 mA
| Breaking capacity | 6 kA
| Rated voltage (Ue) | 230 V AC
| Frequency | 50/60 Hz
| Residual current type | Type AC or Type A (model dependent)
| Mounting | 35 mm DIN rail
| Protection degree | IP20 (installed in enclosure)
| Mechanical endurance | ≥ 10,000 operations
| Electrical endurance | ≥ 4,000 operations
| Terminal type | Screw clamp terminals
| Standards | IEC 61009-1
6 | Uninterruptible Power Supply (UPS), 4 kVA
| Product type | Uninterruptible Power Supply (UPS)
| Rated power capacity | 4 kVA
| Active power (typical) | 3.2–3.6 kW (depending on power factor 0.8–0.9)
| UPS topology | Online double-conversion / Line-interactive (model dependent)
| Input voltage | 220–240 V AC
| Input frequency | 50/60 Hz (auto sensing)
| Output voltage | 230 V AC ±1–2%
| Output frequency | 50/60 Hz ±0.1 Hz (online type)
| Waveform | Pure sine wave
| Transfer time | 0 ms (online) / 2–10 ms (line-interactive)
| Battery type | Sealed lead-acid (VRLA) or external battery pack
| Battery autonomy | 5–15 minutes at full load (extendable with external batteries)
| Recharge time | 4–8 hours to 90% capacity
| Bypass | Automatic and manual bypass (model dependent)
| Efficiency | ≥ 90% (online), ≥ 95% (eco mode)
| Protection features | Overload, short-circuit, battery deep discharge, overtemperature
| Communication ports | USB / RS-232 / SNMP (optional network card)
| Display | LCD display with load and battery status
| Cooling | Forced air cooling (internal fans)
| Installation type | Tower or Rack-mount (model dependent)
| Protection class | IP20 (indoor use)
| Operating temperature | 0 °C to +40 °C
| Standards / Compliance | IEC 62040-1, IEC 62040-2, CE

## Low voltage
No. | Patameter | Specification | Bidder’s response
|  |  | Compliance with technical specifications |  | Technical Compliance (indicate the technical specifications of the proposed items)
|  |  | Yes, we comply | No, we do not comply (indicate discrepancies)
ITB26/03226 Capital repair and modernization of the “Emil Nicula” Theoretical Lyceum from Mereni village, Anenii Noi district. First phase.
1 | Videoregistrator 2U 4K NVR, 128-ch IP camera inputs MP/32-ch@1080p, 2 HDMI, 2 VGA, 8K or dual 4K video outputs,
| Product type | Network Video Recorder (NVR)
| Form factor | 2U rack-mount
| IP camera inputs | 128 channels
| Max recording resolution | Up to 32 MP
| Decoding capability | 2-ch @ 32 MP / 2-ch @ 24 MP / 4-ch @ 12 MP / 8-ch @ 8 MP / 16-ch @ 4 MP / 32-ch @ 1080p
| Video outputs | 2 × HDMI, 2 × VGA
| Display resolution | Up to 8K (7680×4320) or dual 4K (3840×2160) output
| Video compression | H.265+ / H.265 / H.264+ / H.264
| Recording bandwidth (incoming) | Typically up to 400–512 Mbps (model dependent)
| Outgoing bandwidth | Up to 400 Mbps (model dependent)
| Audio support | 2-way audio (RCA), IP camera audio
| Hard drive bays | 8–16 SATA interfaces (model dependent)
| Max storage capacity | Up to 10–16 TB per HDD (model dependent)
| RAID support | RAID 0/1/5/6/10 (enterprise models)
| Network interface | 2 × RJ45 10/100/1000 Mbps (Gigabit)
| USB ports | USB 2.0 / USB 3.0
| Alarm inputs/outputs | Multiple alarm I/O (model dependent)
| Smart functions | Motion detection, intrusion detection, face recognition, smart analytics (AI models)
| Remote access | Web browser, CMS software, mobile app
| Power supply | 100–240 V AC, 50/60 Hz
| Power consumption | Approx. 30–60 W (without HDDs)
| Operating temperature | -10 °C to +55 °C
| Protection class | Indoor use
2 | Hikvision DS‑2CD1067G2‑LUF or equivalent (a 6 MP outdoor/indoor fixed network camera with built-in mic and audio support
| Product type | Fixed network (IP) dome camera
| Image sensor | 1/2.7″ Progressive CMOS
| Resolution | 6 MP (3072 × 2048)
| Lens | Fixed 2.8 mm (wide) / optional 4 mm variants
| Field of View (approx.) | 102° (H) × 55° (V) × 124° (D)
| Min. Illumination | 0.01 lux @ (F1.2, AGC ON)
| Day/Night | IR cut filter with auto switch
| IR Range | Up to 10–15 m (model dependent)
| Video Compression | H.265 / H.264 / MJPEG
| Max. Frame Rate | 6 MP @ 20 fps
| Video Streaming | 3 concurrent streams
| WDR | Digital WDR (Wide Dynamic Range)
| BLC / HLC | Yes (Backlight / Highlight compensation)
| Noise Reduction | 3D Digital Noise Reduction (3D DNR)
| Audio | Built-in microphone
| Network | 1 × RJ45 10/100 Mbps
| PoE | 802.3af PoE (power over Ethernet)
| Storage | MicroSD/SDHC/SDXC card slot (up to 256 GB)
| Smart features | Motion detection, region of interest, privacy mask
| ONVIF | Profiles S/G compatible
| Power | PoE or 12 V DC
| Operating Temp. | –30 °C to +60 °C
| Ingress Protection | IP67 (dust & water resistant)
| IK Rating | IK10 (impact resistant)
| Housing material | Metal / plastic weatherproof casing
| Dimensions | Approx. Ø109 × 78 mm
| Weight | ~0.4 kg
3 | Hikvision DS-2CD1147G2H-LIU(F), a 4 MP network camera with built-in IR and advanced features or equivalent
| Product type | Network (IP) turret camera
| Image sensor | 1/3″ Progressive Scan CMOS
| Effective pixels | 4 MP (2688 × 1520)
| Lens | 2.8 mm fixed lens (horizontal FOV ~102°)
| Maximum resolution | 2688 × 1520
| Min. illumination | 0.005 lux @ (F1.6, AGC ON)
| Day/Night | True D/N with mechanical IR cut filter
| IR illumination | Up to 30 m range (built-in IR LEDs)
| Video compression | H.265 / H.264 / MJPEG
| Max. frame rate | 4 MP @ 30 fps
| Video streams | 3 independent streams
| Wide Dynamic Range | Digital WDR (120 dB)
| Noise reduction | 3D DNR (Digital Noise Reduction)
| ROI / BLC / HLC | Yes (Region of Interest / Backlight / Highlight Comp)
| Audio | Built-in microphone
| Smart features | Motion detection, line crossing, intrusion detection (model dependent)
| Network | 1 × RJ45 10/100 Mbps
| Power | PoE (802.3af) or 12 V DC
| Power consumption | < 6 W typically
| On-board storage | MicroSD/SDHC/SDXC up to 256 GB
| Operating temp. | –30 °C to +60 °C
| Ingress protection | IP67 weatherproof
| Impact protection | IK10 vandal resistant
| Housing material | Metal base with plastic/metal dome
| Dimensions | Approx. Ø110 × 93 mm
| Weight | ~0.5 kg
4 | Hikvision DS‑3E1510P‑SI, an 8-port Gigabit PoE-capable network switch often used in IP camera systems or equivalent
| Product type | Smart managed PoE network switch
| Ports – Ethernet | 8 × Gigabit RJ45 PoE ports
| Ports – Uplink | 2 × Gigabit optical fiber (SFP) ports
| Switching capacity | 20 Gbps
| Packet forwarding rate | 14.88 Mpps
| MAC address table | 8 K entries
| Internal packet cache | 4.1 Mbits
| PoE standards | IEEE 802.3af / IEEE 802.3at
| PoE power per port | Up to 30 W per PoE port
| Total PoE budget | 110 W
| PoE power pins | End-span 1/2(+), 3/6(-)
| Long-range PoE | Ports 1–8 up to 300 m (extend mode)
| Surge protection | 6 kV on PoE ports
| Network functions | STP/RSTP, VLAN, SNMP, QoS, link aggregation
| PoE watchdog | Auto-detect & restart unresponsive cameras
| Operating temperature | 0 °C to 40 °C
| Storage temperature | –40 °C to 85 °C
| Operating humidity | 5 % to 95 % (no condensation)
| Power supply | 48 V DC, 2.5 A
| Max. power consumption | 120 W
| Idle power | ~7 W
| Dimensions (W×H×D) | 217.6 × 27.8 × 108.55 mm
| Weight | ~1.21 kg
| Installation | Desktop or wall mount
| Certifications | CE, FCC, UL, RoHS, WEEE, RCM
5 | Hikvision DS-3E1326P-EI/M or equivalent
| Device Type | Smart Managed PoE Switch
| Ports (PoE) | 24 × 10/100 Mbps RJ45
| Uplink Ports | 1 × Gigabit RJ45 + 1 × Gigabit RJ45/SFP Combo
| PoE Standard | IEEE 802.3af / 802.3at
| Max PoE per Port | 30 W
| Total PoE Budget | 230 W
| Switching Capacity | 14.8 Gbps
| Packet Forwarding Rate | 11.01 Mpps
| MAC Address Table | 16K
| Packet Buffer | 4 Mbit
| VLAN Support | 802.1Q (up to 4094 VLANs)
| Link Aggregation | Static (1 group)
| Loop Prevention | STP / RSTP
| Long Range PoE Mode | Up to 300 m (with supported devices)
| PoE Watchdog | Yes (auto restart of unresponsive devices)
| Port Isolation | Yes
| Management | Web GUI, LLDP, Port Mirroring, Cable Diagnostics, Hik-Central / Hik-Partner Pro
| Surge Protection | 6 kV
| Power Supply | 100–240 VAC, 50/60 Hz
| Max Power Consumption | ~250 W
| Idle Consumption | ~20 W
| Operating Temperature | 0°C to +45°C
| Storage Temperature | −40°C to +85°C
| Humidity | 5–95% (non-condensing)
| Dimensions (W×H×D) | 440 × 44 × 220.8 mm
| Weight | ~2.13 kg
| Mounting | 19" Rack-mountable
6 | Hard Disk Drive (HDD) 8 TB SATA-III (3.5″ form-factor, internal storage)
| Capacity | 8 TB (≈ 8 000 GB)
| Interface | SATA-III (6 Gb/s)
| Form Factor | 3.5″
| Rotational Speed | 5400 rpm (desktop/consumer) / 7200 rpm (performance/enterprise)
| Cache (Buffer) | 128 MB – 256 MB
| Max Transfer Rate (SATA) | Up to 6.0 Gb/s
| Sustained Data Transfer | ~215 – 240 MB/s (model dependent)
| Mean Time Between Failures (MTBF) | ~1 M – 2.5 M hours (enterprise grade)
| Power Consumption (Typical) | ~5 – 9 W during read/write
| Idle Power | ~3 – 7 W
| Voltage | 5 V / 12 V (standard SATA power)
| Operating Temp. | ~0 °C – 60 °C
| Shock (Operating) | ~70 G
| Dimensions (W×D×H) | ~101.6 × 147 × 26.1 mm
| Weight | ~650 – 780 g
| Features | S.M.A.R.T., advanced power management, error recovery controls
7 | Audio Monitoring & Processing Server
| CPU | Intel Core i9 (12th/13th Gen+) or equivalent Xeon / AMD Ryzen 9
| Cores / Threads | Min. 16 cores / 24 threads
| RAM | 64 GB DDR4 / DDR5 (ECC recommended for stability)
| GPU | NVIDIA RTX 3060 (12GB VRAM) or higher
| System Storage | 1TB NVMe SSD (PCIe Gen3/Gen4)
| Additional Storage (Optional) | 4–8TB HDD for audio archiving
| Network | 2 × Gigabit Ethernet (RJ45)
| Operating System | Ubuntu Server 22.04 LTS or Windows Server 2022
| Power Supply | 750W 80+ Gold PSU
| Chassis | 2U Rackmount or Tower Workstation
| Cooling | High-performance CPU cooling + optimized airflow for GPU
| Redundancy (Optional) | RAID 1 for SSD / redundant PSU
8 | Louroe Digifact A (LE-870) IP audio microphone
| Device Type | Ceiling Mount Digital IP Microphone with Audio Analytics
| Microphone Type | Electret condenser (dynamic audio capture)
| Pickup Pattern | Omnidirectional (one-way audio capture)
| Audio Coverage | Approx. 30 ft (≈ 9.1 m) diameter circle
| Sensitivity | –45 dBV/Pa (1 Pa = 94 dB SPL)
| Frequency Response | 50 Hz – 15 kHz
| Audio Streaming | One-way audio (RTSP compatible)
| Audio Compression | PCM 16-bit, G.711 a-Law & µ-Law, G.726-40, AAC
| Network Interface | 1 × RJ45 (10/100 Mbps) – PoE powered
| Power | PoE IEEE 802.3af (Optional external 5 V DC input)
| Protocols Supported | IPv4, HTTP, RTSP, RTP, TCP, SSH, ONVIF S & T
| Audio Analytics | Built-in analytics (dB threshold, aggression, glass break, car alarm, etc.)
| API | Open API for integration with VMS / third-party software
| Event Actions | TCP notification, external output, pre/post audio recording to NAS
| Memory | 512 MB RAM (typical)
| Environmental | Operating: –20 °C to +50 °C, 10–85% RH
| Dimensions | Ø 119 × 50.8 mm (diameter × height)
| Weight | Approx. 255 g (9 oz)
| Mounting | Ceiling / wall mount (included plate & hardware)
| Certifications | NDAA compliant (in some regions)
| Included Accessories | User manual, 5-pin & 2-pin headers
9 | Ubiquiti UniFi U7 Pro Outdoor Wi-Fi 7 outdoor access point or equivalent
| Device Type | Outdoor Wi-Fi 7 Tri-Band Access Point
| Wi-Fi Standard | Wi-Fi 7 (802.11be), backward compatible with 802.11a/b/g/n/ac/ax
| Frequency Bands | 2.4 GHz, 5 GHz, 6 GHz
| Spatial Streams | 6 (2×2 MU-MIMO each band)
| Total Throughput | ~10.7–10.8 Gbps aggregated
| Max Data Rates | 6 GHz: ~5.7–5.8 Gbps
5 GHz: ~4.3–8.6 Gbps
2.4 GHz: ~688 Mbps
| Antenna Gain | Internal directional:
• 2.4 GHz: ~8 dBi
• 5 GHz: ~11 dBi
• 6 GHz: ~10 dBi
| External Antennas | Omni antennas included (varies by region)
| MU-MIMO | DL/UL MU-MIMO on all bands
| Coverage | ~465 m² (≈ 5 000 ft²) in open space
| Max Clients | 300+ simultaneous clients
| Ethernet Interface | 1 × 1/2.5 GbE RJ45 (PoE+)
| Power | PoE+ (802.3at), 42.5–57 V DC
| Power Consumption | ~21 W maximum
| Weatherproofing | IPX6; IP67 with cable-gland door kit included
| Operating Temp. | –30 °C to +60 °C
| Operating Humidity | 5 % – 95 % non-condensing
| Dimensions | Without mount: 170 × 208 × 66.5 mm
With mount: 170 × 208 × 121.8 mm
| Weight | ~1.2 kg (device only); ~1.33 kg with mount
| Enclosure Material | UV-stabilized polycarbonate & aluminum alloy
| Mounting Options | Wall or pole mount (included)
| Management | Managed via UniFi Network Controller / App
| Advanced Features | Fast roaming, band steering, meshing, RADIUS/VLAN support, guest portal, Wi-Fi schedules
10 | FortiGate 100F next-generation firewall or equivalent
| Form Factor | 1U Rackmount
| Firewall Throughput | Up to ~20 Gbps (1518-byte UDP)
| IPS Throughput | ~2.6 Gbps
| NGFW Throughput | ~1.6 Gbps
| Threat Protection | ~1 Gbps
| IPsec VPN Throughput | ~11.5 Gbps
| SSL-VPN Throughput | ~750 Mbps
| Concurrent Sessions (TCP) | ~1,500,000
| New Sessions/s (TCP) | ~56,000
| Firewall Policies | 10000
| Virtual Domains (VDOMs) | Default/Max: 10/10
| Interfaces – RJ45 | 12 × GE RJ45 ports
| Interfaces – WAN/DMZ/MGMT/HA | RJ45: 2 × WAN, 1 × DMZ, 1 × Mgmt, 2 × HA
| SFP / SFP+ Slots | 4 × GE SFP + 2 × 10 GE SFP+ FortiLink
| USB Port | 1 × USB
| Console Port | 1 × RJ45
| Power Supply | Dual internal AC (100–240 V) / redundant non-hot-swappable
| Power Consumption | ~26.5 W – 29.5 W
| Heat Dissipation | ~100.6 BTU/h
| Operating Temp. | 0 °C – 40 °C
| Storage Temp. | –35 °C – 70 °C
| Humidity | 10 % – 90 % non-condensing
| Dimensions (HxWxD) | 44 × 432 × 254 mm
| Weight | ~3.29 kg
| Max FortiAPs Supported | Up to 128 (total) / 64 (tunnel mode)
| Max FortiClients Registered | ~600 devices
| High Availability | Active/Active, Active/Passive, Clustering
| Security Features | NGFW, IPS, SSL Inspection, Application Control, Anti-Malware, SD-WAN, ZTNA, Threat Intelligence
11 | Ubiquiti UniFi Switch Pro Aggregation (high-capacity aggregation switch) or equivalent
| Device Type | Managed Layer-3 Aggregation Switch
| Ports | 28 × 1/10 Gbps SFP+
4 × 1/10/25 Gbps SFP28
| Total Non-Blocking Throughput | 380 Gbps
| Switching Capacity | 760 Gbps
| Forwarding Rate | 565.44 Mpps
| Layer Features | Static routing, inter-VLAN routing, DHCP server
| Management Interface | In-band Ethernet + UniFi Network Controller / App
| Touchscreen Display | 1.3″ AR LCM color touchscreen
| Power Supply | Internal AC/DC 100–240 V
| Max Power Consumption | ~100 W
| PoE Support | No PoE output (fiber/DAC connectivity only)
| Enclosure | 1U rack-mountable steel chassis
| Dimensions (WxDxH) | 442 × 325 × 44 mm
| Weight | ~4.6 kg (4.7 kg with mounting brackets)
| Environmental (Operating) | –5 °C to +40 °C, 10–90% non-condensing
| ESD/EMP Protection | Air: ±16 kV; Contact: ±12 kV
| Certifications | CE, FCC, IC
12 | Ubiquiti UniFi Switch Pro Aggregation (high-capacity aggregation switch) or equivalent
| Device Type | Managed Layer-2/L2+ Ethernet Switch
| Form Factor | 1 RU Rack-mount
| Total Ports | 48 × GE RJ45 + 4 × 10GE SFP+ uplinks
| Console Port | 1 × RJ45
| PoE Support | None (0 PoE ports)
| Switching Capacity (duplex) | 176 Gbps
| Max Packets Forwarding | 260 Mpps (million packets per second)
| MAC Address Table Size | 32 K entries
| Network Latency | < 1 µs
| VLAN Support | Up to 4 K VLANs
| Link Aggregation | LAG size up to 8 / up to 128 groups
| Packet Buffer | 2 MB
| DRAM Memory | 512 MB DDR3
| Flash Memory | 64 MB
| ACL Entries | ~640‒768 (varies by datasheet)
| Spanning Tree Instances | 16 – 32 supports (varies)
| Management | FortiLink (via FortiGate), GUI, CLI, SNMP, API
| Layer-2 Features | VLAN, STP/RSTP/MSTP, LACP, IGMP Snooping, 802.1x, Port Mirroring
| Layer-3 Lite | Static routing & basic L3 functions (varies by firmware)
| Power Supply | Internal AC 100–240 V
| Typical Power Consumption | ~55.8 W / Max ~57 W
| Dimensions (H×D×W) | 44 × 260 × 440 mm
| Weight | ~3.46 kg
| Operating Temp. | 0 – 45 °C (32 – 113 °F)
| Humidity | 10 % – 90 % non-condensing
| Airflow | Side-to-back
| Certifications | CE, FCC, UL, RoHS2
13 | Ubiquiti UniFi Switch Pro 24 PoE (USW-Pro-24-PoE) or equivalent
| Device Type | Managed PoE Ethernet Switch
| Form Factor | 1U Rackmount / Desktop
| Total Ports | 24 × Gigabit RJ45
| PoE Ports | 24 × PoE+ (802.3af/at), up to 30 W per port
| Uplink Ports | 2 × 10 Gbps SFP+/RJ45 (combo)
| Aggregate PoE Budget | 400 W (typical)
| Switching Capacity | 128 Gbps
| Forwarding Rate | ~95.24 Mpps
| Layer | Layer 2 with Layer 3 Lite features
| VLAN Support | Yes (802.1Q)
| Link Aggregation | LACP supported
| Management | UniFi Network Controller / UniFi App
| Touchscreen Display | Yes (front LCD touchscreen)
| PoE Modes Supported | 802.3af, 802.3at
| Max PoE Per Port | 30 W
| PoE Power Management | Per-port priority & scheduling
| L2 Features | STP/RSTP/MSTP, IGMP Snooping, QoS
| Layer 3 Features | Static routing, DHCP server
| Network Protection | IPv4/IPv6 ACLs
| Environmental (Operating) | 0–40 °C, 10–90 % non-condensing
| Power Supply | Internal AC 100–240 V
| Power Consumption | ~450 W (max under PoE load)
| Dimensions (W×D×H) | ~442 × 257 × 44 mm
| Weight | ~4.5 kg
| Mounting Options | Rack, Wall, Desktop
| Certifications | CE, FCC, IC
14 | APC Smart‑UPS Ultra On‑Line series of high-performance uninterruptible power supplies (UPS)
| UPS Topology | Double-conversion On-Line (true online UPS) with pure sine wave output
| Input Voltage Range | ~187 – 275 V AC (model dependent)
| Input Frequency | 40 – 70 Hz auto-sense
| Output Power Capacity | Range from ~2200 VA/2200 W up to ~8000 VA/8000 W (specific by SKU)
| Nominal Output Voltage | 220/230/240 V AC (region dependent)
| Output Waveform | Pure sine wave (ideal for servers & sensitive electronics)
| Crest Factor | 3:01
| Output Frequency | 50/60 Hz ± 3 Hz sync to mains
| Efficiency (Green Mode) | Up to ~98.5 % (where supported)
| Battery Technology | Lithium-ion (Li-Ion) – long life and high energy density
| Battery Runtime (Typical) | ~5 min at full load (5000 W model); longer at lower loads; expandable with external battery packs
| Battery Life Expectancy | ~8–10+ years
| Recharge Time | ~1.5 hours to full recharge
| Outlets / Connections | IEC 320 C13 & C19 outlets (varies by model) up to 10 on some units
| Management / Communication Ports | USB, Ethernet SmartConnect, network management card embedded (varies)
| Display | Auto-rotating high-resolution LCD panel
| Form Factor | Rackmount / Tower convertible; typical size 1U–4U depending on capacity
| Protection Features | Internal bypass, surge protection, EPO support
| Operating Temp. | ~0 – 40 °C
| Operating Humidity | ~0 – 95 % non-condensing
| Certifications | CE, RoHS, IEC/EN 62040 standards
15 | Yeastar S-412 VoIP PBX or equivalent
| System Type | Hybrid analog + VoIP PBX (small business)
| User Capacity | Up to 20 internal users (mixed analog & VoIP)
| Concurrent Calls | Up to 8 simultaneous calls
| VoIP Trunks | 4 SIP trunks
| Fixed Ports | 8 × FXS RJ11 built-in
| Max FXS Ports | Up to 12 (with modules)
| Customizable Ports | Up to 4 FXO/BRI (external lines)
| Cellular Ports | Up to 2 GSM/3G/4G channels (one data 4G)
| LAN / WAN | 1 × 10/100 Mbps LAN, 1 × 10/100 Mbps WAN
| Network Protocols | SIP (RFC3261), IAX2
| Transport Protocols | UDP, TCP, TLS, SRTP
| Supported Codecs | G.711 (a/u-law), G.722, G.726, G.729A, GSM, Speex, ADPCM, iLBC, H.263/H.264, MPEG4
| DTMF Support | In-band, RFC4733, RFC2833, SIP INFO
| Fax Support | T.30 & T.38; Fax-to-Email
| Storage / Media | TF card slot for recording/storage
| Built-in Features | IVR, Auto provisioning, Voicemail, Call recording, Queues, Conferencing, LDAP server, Email/SMS alerts, CDR/Billing, CRM/Hotel/Apps support
| Linkus UC Support | Yes – mobile/desktop unified comms client
| Remote Management | Secure remote monitoring/management tool
| Power Supply | 12 V DC, 3.33 A (approx.)
| Power Consumption | ~9.0 – 25.6 W
| Dimensions | ~290 × 180 × 33 mm
| Weight | ~0.68 kg
| Operating Temp. | 0 – 40 °C
| Humidity | 10 – 90 % non-condensing
| Mounting | Desktop & wall mount
| Installation | Plug-and-play setup with intuitive web GUI
| Security | Built-in firewall, TLS/SRTP encrypted signalling/audio
16 | INIM Previdia UltraVox — an integrated fire detection + voice evacuation (EVAC) + public address system or equivalent
| Product Type | Integrated fire detection & EVAC control panel
| Standards / Certifications | EN54-2 (control panel), EN54-4 (power supply), EN54-16 (voice alarm EVAC), EN54-21 (networked systems), EN12094-1 (gas extinguishing interfaces)
| Architecture | Modular (expandable up to 4 cabinets, up to 32 IFM/IFAM modules)
| Integrated Functions | Fire detection, alarm, voice evacuation (EVAC), public address (PA), audio entertainment
| Base Modules Included | FPMCPU control unit, FPAMIAS EVAC control, IFAMPSU power supply 1000 W, IFAMEVAC audio matrix, IFAMAMP 250 W amplifier, IFM2L loop module, PTT microphone
| Power Supply Voltage | 90 – 264 VAC, 47 – 63 Hz
| Maximum Current Draw | 8.5 A @ 115 VAC; 5 A @ 230 VAC
| DC Output Voltage | 26 V DC nominal (20 – 27.6 V)
| Speaker Line Output Voltage | 100 Vrms
| Maximum Power per PSU Module | 1000 W (expandable to 4000 W with 4 cabinets)
| Max Current from PSU Module | 38 A (35 A available to system)
| Battery Support | 2 × 12 V batteries (17 Ah or 38 Ah)
| Speaker Line Supervision | 20 kHz pilot tone (no EOL needed above 20 W)
| Network Interfaces | IDANET (Ethernet or fiber), optional Hornet+ RS485 or TCP/IP connection
| Audio Zones Supported | Up to ~1000 audio zones (system capable when expanded)
| Audio Sources / Control | 8 local digital audio tracks + 8 network digital audio tracks
| Analog Audio Inputs | 2 × analog music inputs + 2 × AUX inputs with priority detection
| Amplifier Support | Up to ~30 × Class-D 250 W amplifiers in network
| Display | Dual 7″ color touchscreen displays (65,000 colours)
| Cabinet / Enclosure | PRCAB+ modular cabinet (IP30)
| Protection / IP Rating | IP30
| Operating Temperature | −5 °C .. +40 °C
| Dimensions | 675 × 430 × 260 mm (per cabinet)
| Weight | ~23 kg (without batteries)
| Color Options | RAL7042 (grey) or RAL3001 (red)
| Event / Log Capability | Stores recent fire & EVAC events (typically thousands)
| Expansion / Networking | Up to 48 control panels via IDANET, shared audio across network
17 | INIM ED100 – Addressable Optical Smoke Detector (EN54-7) or equivalent
| Product Type | Addressable optical (photoelectric) smoke detector
| Standard Compliance | EN54-7 / EN54-17 (with isolator) compatible
| Sensor Type | Optical chamber using scattered light (Tyndall effect)
| Power Supply | 19 – 30 V DC
| Current Draw (Standby) | ~200 µA
| Current Draw (Alarm) | ~10 mA @ 27.6 V
| Output Contact (Isolator) | Max 14 mA (internally limited)
| Sensitivity Settings | Adjustable: 0.08, 0.10, 0.12 (default), 0.15 dB/m
| Addressing | Manual address selection (1–240)
| Operating Temp. | –5 °C to +40 °C
| Humidity (non-condensing) | Up to 95 % RH
| Dimensions (Ø × H) | 110 mm × 46 mm (with base)
| Weight | ~160 g (with base); ~90 g (without base)
| Mounting | Compatible base (e.g., EB0010) for addressable loop
| Loop Connectivity | 2-wire twisted/shielded between fire panel and detector
18 | INIM IL0010 remote alarm indicator — a visual LED repeater used in fire alarm systems or equivalent
| Type | Remote LED indicator (alarm visual repeater)
| Purpose | Replicates detector alarm signals visually at a remote location
| Compatible With | Addressable detectors (ENEA series) and conventional detectors (IRIS series)
| Power Supply | 19‒30 V DC
| Current Consumption (Alarm) | ~20 mA @ 27.6 V DC
| Signal Type | LED optical flash indicator (visual alarm)
| Housing Material | ABS plastic
| Protection Rating | IP42 (indoor use protection)
| Operating Temperature | –5 °C to +40 °C
| Humidity (non-condensing) | Up to 95 % RH
| Dimensions (W×H×D) | ~79 × 76 × 27 mm
| Weight | ~45 g
| Mounting | Wall or ceiling mount near detector location
| Certifications | CE declaration of conformity (EU)
19 | INIM ES0020RE – Addressable Loop-Powered Siren with Flash or equivalent
| Device Type | Addressable loop-powered siren + strobe (audible/visual indicator)
| Protocol | Enea / Inim addressable fire alarm loop
| Power Supply (Loop Powered) | 17 – 60 V DC
| Current Consumption | 4 – 41 mA (depending on tone selected)
| Beacon Current | ~5 mA (visual flash)
| Sound Output (at 1 m) | Up to ~106 dB(A) (adjustable based on tone)
| Tones | 32 selectable tones (via DIP switch or programming)
| Protocol Module Included | EU311S (loop isolator module included)
| Protection Rating | IP65 / IP67 (weatherproof – suitable for outdoor use)
| Operating Temperature | −25 °C to +70 °C
| Color | Red housing
| Certifications | EN54-3 (audible alarm), EN54-17/18 (loop & visual where applicable)
| Mounting | Direct installation on fire alarm loop with supplied base
| Typical Dimensions (approx.) | Ø ~98 mm × height ~104 mm
| Weight (approx.) | ~250 g